## Toroidal
CORE SIZE CALCULATION
|  | Data to be Input | Remarks |  | Output Data | Remarks
Height/Width of the Sheet (mm) |  | 95 | See diagram below | Toroidal Core Cross Sectional Area (sq-mm) | 9737.5 | Red portion of diagram
Thickness of the Sheet (mm) |  | 0.27 |  | Effective Core Cross Sectional Area (sq-mm) | 7105.7432
Outside Diameter of Toroidal Core (mm) |  | 325 | See diagram below | Length of Seet required (meters) | 193.6429
Inside Diameter of Toroidal Core (mm) |  | 120 | See diagram below | Weight of the Core (kgs) | 37.9971 | 7,650 kgs/cubic meter
Inter Layer Air Gap (mm) |  | 0.1 |  | Power Handling Capacity of Core (Watts) | 8533.0782
|  |  |  | Inner Circumference of Core (mm) | 376.9908
|  |  |  | Outer Circumference of Core (mm) | 1021.0168
Core is made of long length of silicon sheet, spirally wound layer by layer until the required outer dia is achieved |  |  |  | Core Thickness (mm) | 102.5 | Red portion of diagram
|  |  |  | Number of Turns of Spiral Winding for Core | 277.027
WINDING CALCULATION
Primary Winding Voltage (VAC) | 230
Secondary Winding Voltage (VAC) | 28 |  |  | Turns Ratio | 8.2143
Rated Power Output (Watts) | 6000 |  | Must be <= I4 | Turns/Volt | 0.42262 | Using Standard Formula
Secondary Winding Current @ Rated Power (Amps) | 214.2857 |  | Pls. see Note below | Turns/Volt (Simplified Formula) | 0.45315
Primary Winding Current @ Rated Power (Amps) | 30.6905 |  | 85% Efficiency | No. of Turns (Primary) | 100.7137
Frequency (Hz) | 50 |  |  | No. of Turns (Secondary) | 12.2608
Flux Density (Tesla) | 1.5 |  |  | Length of Primary Winding Wire (meters) | 44.5557 | First Layer
|  |  |  | Length of Secondary Winding Wire (meters) | 5.8116 | Second Layer
Note: |  |  |  | Primary Winding Wire Area (sq-mm) | 15.3453 | @ 2.0 Amps/sq-mm
The peak secondary current would be 150 Amps. |  |  |  | Secondary Winding Wire Area (sq-mm) | 107.1429 | @ 2.0 Amps/sq-mm
Therefore wire dia of secondary winding will need to
be determined accordingly.

## E-I
Input data: |  | Iron: | Center leg mm: |  | 60 |  | Design decisions: |  | Flux Density T: |  | 1.2
|  |  | Stack height mm: |  | 100 |  |  |  | mm2/A: |  | 0.5
|  |  | Loss W/kg@1T,50Hz: |  | 2.5 |  |  |  | Fill factor: |  | 0.4
[9 empty] | Temperature rise K: |  | 70
|  |  | Primary V: |  | 28
|  |  | Secondary no-load V: |  | 231
|  |  | Frequency Hz: |  | 50
[7 empty] | Prices: |  | Iron Rs./kg |  | 130
[9 empty] | Copper Rs./kg |  | 1350
Output data: |  | Cross section mm2: |  | 6000 |  | Window area mm2: |  | 2700 |  | Copper area mm2: |  | 1080
|  | Turns per Volt: |  | 0.62563 |  | Av. turn length mm: |  | 414.2478
| Primary | turns: | 17.5175 |  | Length m: | 7.2566 |  | mm2: | 30.8263 |  | Ampere: | 61.6526 | 1726.272
| Secondary | turns: | 144.5195 |  | Length m: | 59.8669 |  | mm2: | 3.7365 |  | Ampere: | 7.473 | 1726.272
| Input power VA: |  | 4000 | [5 empty] | Iron loss W: |  | 59.8752
| Power loss %: |  | 3.5702 | [5 empty] | Copper loss W: |  | 82.9325
| Voltage drop %: |  | 2.0733 | [5 empty] | Total loss W: |  | 142.8077
| Loaded Vout: |  | 226.2106 | [5 empty] | Surface area m2: |  | 0.12024
|  |  |  | Cost |  |  | Required thermal transfer coefficient W/m2K: |  |  |  | 16.967
| Iron weight kg: |  | 16.632 | 2162.16 | [5 empty] | 7 is easy to get
| Copper weight kg: |  | 3.9952 | 5393.4812 | [5 empty] | Convection cooling up to 12
| Cost Rs. |  | 20.6272 | 7555.6412 | [5 empty] | Strong fan up to 30
| Rs./W: |  | 1.8889 | [6 empty] | Oil up to 50?